## 420_7MM
S&C Fault Fiter Electronic Power Fuses | [7 empty] | S&C Fault Fiter Electronic Power Fuses | [7 empty] | S&C Fault Fiter Electronic Power Fuses | [7 empty] | S&C Fault Fiter Electronic Power Fuses
Compound-Curve-Type Control Module (TCC 420-7) | [7 empty] | Compound-Curve-Type Control Module (TCC 420-7) | [7 empty] | Compound-Curve-Type Control Module (TCC 420-7) | [7 empty] | Compound-Curve-Type Control Module (TCC 420-7)
Total Clearing Time-Current Characteristic Curve Dated September 8, 1986 | [7 empty] | Total Clearing Time-Current Characteristic Curve Dated September 8, 1986 | [7 empty] | Total Clearing Time-Current Characteristic Curve Dated September 8, 1986 | [7 empty] | Total Clearing Time-Current Characteristic Curve Dated September 8, 1986
Tolerance: Curves are plotted to maximum test points. All variations are minus | [7 empty] | Tolerance: Curves are plotted to maximum test points. All variations are minus | [7 empty] | Tolerance: Curves are plotted to maximum test points. All variations are minus | [7 empty] | Tolerance: Curves are plotted to maximum test points. All variations are minus
Short Time Delay Band: 1 | [7 empty] | Short Time Delay Band: 2 | [7 empty] | Short Time Delay Band: 3 | [7 empty] | Short Time Delay Band: 4
Min P/U = 400A |  | Min P/U = 600A |  | Min P/U = 800A |  | Min P/U = 1100A |  | Min P/U = 400A |  | Min P/U = 600A |  | Min P/U = 800A |  | Min P/U = 1100A |  | Min P/U = 400A |  | Min P/U = 600A |  | Min P/U = 800A |  | Min P/U = 1100A |  | Min P/U = 400A |  | Min P/U = 600A |  | Min P/U = 800A |  | Min P/U = 1100A
Current | Time | Current | Time | Current | Current | Current | Time | Current | Time | Current | Time | Current | Current | Current | Time | Current | Time | Current | Time | Current | Current | Current | Time | Current | Time | Current | Time | Current | Current | Current | Time
8424.74 | 0.01 | 8424.74 | 0.01 | 8424.74 | 0.01 | 8424.74 | 0.01 | 8424.74 | 0.01 | 8424.74 | 0.01 | 8424.74 | 0.01 | 8424.74 | 0.01 | 8424.74 | 0.01 | 8424.74 | 0.01 | 8424.74 | 0.01 | 8424.74 | 0.01 | 8424.74 | 0.01 | 8424.74 | 0.01 | 8424.74 | 0.01 | 8424.74 | 0.01
8424.74 | 0.014844 | 8424.74 | 0.014844 | 8424.74 | 0.014844 | 8424.74 | 0.014844 | 8424.74 | 0.014844 | 8424.74 | 0.014844 | 8424.74 | 0.014844 | 8424.74 | 0.014844 | 8424.74 | 0.014844 | 8424.74 | 0.014844 | 8424.74 | 0.014844 | 8424.74 | 0.014844 | 8424.74 | 0.014844 | 8424.74 | 0.014844 | 8424.74 | 0.014844 | 8424.74 | 0.014844
8391.11 | 0.020876 | 8391.11 | 0.020876 | 8391.11 | 0.020876 | 8391.11 | 0.020876 | 8391.11 | 0.020876 | 8391.11 | 0.020876 | 8391.11 | 0.020876 | 8391.11 | 0.020876 | 8391.11 | 0.020876 | 8391.11 | 0.020876 | 8391.11 | 0.020876 | 8391.11 | 0.020876 | 8391.11 | 0.020876 | 8391.11 | 0.020876 | 8391.11 | 0.020876 | 8391.11 | 0.020876
8249.67 | 0.024695 | 8249.67 | 0.024695 | 8249.67 | 0.024695 | 8249.67 | 0.024695 | 8249.67 | 0.024695 | 8249.67 | 0.024695 | 8249.67 | 0.024695 | 8249.67 | 0.024695 | 8249.67 | 0.024695 | 8249.67 | 0.024695 | 8249.67 | 0.024695 | 8249.67 | 0.024695 | 8249.67 | 0.024695 | 8249.67 | 0.024695 | 8249.67 | 0.024695 | 8249.67 | 0.024695
8029.91 | 0.025625 | 8029.91 | 0.025625 | 8029.91 | 0.025625 | 8029.91 | 0.025625 | 8029.91 | 0.025625 | 8029.91 | 0.025625 | 8029.91 | 0.025625 | 8029.91 | 0.025625 | 8029.91 | 0.025625 | 8029.91 | 0.025625 | 8029.91 | 0.025625 | 8029.91 | 0.025625 | 8029.91 | 0.025625 | 8029.91 | 0.025625 | 8029.91 | 0.025625 | 8029.91 | 0.025625
7894.55 | 0.029832 | 7894.55 | 0.029832 | 7894.55 | 0.029832 | 7894.55 | 0.029832 | 7894.55 | 0.029832 | 7894.55 | 0.029832 | 7894.55 | 0.029832 | 7894.55 | 0.029832 | 7894.55 | 0.029832 | 7894.55 | 0.029832 | 7894.55 | 0.029832 | 7894.55 | 0.029832 | 7894.55 | 0.029832 | 7894.55 | 0.029832 | 7894.55 | 0.029832 | 7894.55 | 0.029832
7792.59 | 0.033168 | 7792.59 | 0.033168 | 7792.59 | 0.033168 | 7792.59 | 0.033168 | 7792.59 | 0.033168 | 7792.59 | 0.033168 | 7792.59 | 0.033168 | 7792.59 | 0.033168 | 7792.59 | 0.033168 | 7792.59 | 0.033168 | 7792.59 | 0.033168 | 7792.59 | 0.033168 | 7792.59 | 0.033168 | 7792.59 | 0.033168 | 7792.59 | 0.033168 | 7792.59 | 0.033168
7258.5 | 0.035219 | 7258.5 | 0.035219 | 7258.5 | 0.035219 | 7258.5 | 0.035219 | 7258.5 | 0.035219 | 7258.5 | 0.035219 | 7258.5 | 0.035219 | 7258.5 | 0.035219 | 7258.5 | 0.035219 | 7258.5 | 0.035219 | 7258.5 | 0.035219 | 7258.5 | 0.035219 | 7258.5 | 0.035219 | 7258.5 | 0.035219 | 7258.5 | 0.035219 | 7258.5 | 0.035219
7258.5 | 0.043362 | 7258.5 | 0.043362 | 7258.5 | 0.043362 | 7258.5 | 0.043362 | 7258.5 | 0.043362 | 7258.5 | 0.043362 | 7258.5 | 0.043362 | 7258.5 | 0.043362 | 7258.5 | 0.043362 | 7258.5 | 0.043362 | 7258.5 | 0.043362 | 7258.5 | 0.043362 | 7258.5 | 0.043362 | 7258.5 | 0.043362 | 7258.5 | 0.043362 | 7258.5 | 0.043362
7258.5 | 0.066659 | 7258.5 | 0.066659 | 7258.5 | 0.066659 | 7258.5 | 0.066659 | 7258.5 | 0.066659 | 7258.5 | 0.066659 | 7258.5 | 0.066659 | 7258.5 | 0.066659 | 7258.5 | 0.066659 | 7258.5 | 0.066659 | 7258.5 | 0.066659 | 7258.5 | 0.066659 | 7258.5 | 0.066659 | 7258.5 | 0.066659 | 7258.5 | 0.066659 | 7258.5 | 0.066659
7258.5 | 0.085592 | 7258.5 | 0.085592 | 7258.5 | 0.085592 | 7258.5 | 0.085592 | 7258.5 | 0.085592 | 7258.5 | 0.085592 | 7258.5 | 0.085592 | 7258.5 | 0.085592 | 7258.5 | 0.085592 | 7258.5 | 0.085592 | 7258.5 | 0.085592 | 7258.5 | 0.085592 | 7258.5 | 0.085592 | 7258.5 | 0.085592 | 7258.5 | 0.085592 | 7258.5 | 0.085592
7258.5 | 0.092166 | 7258.5 | 0.092166 | 7258.5 | 0.092166 | 7258.5 | 0.092166 | 7258.5 | 0.092166 | 7258.5 | 0.092166 | 7258.5 | 0.092166 | 7258.5 | 0.092166 | 7258.5 | 0.092166 | 7258.5 | 0.092166 | 7258.5 | 0.092166 | 7258.5 | 0.092166 | 7258.5 | 0.092166 | 7258.5 | 0.092166 | 7258.5 | 0.092166 | 7258.5 | 0.092166
6788.11 | 0.094688 | 6788.11 | 0.094688 | 6788.11 | 0.094688 | 6788.11 | 0.094688 | 7258.5 | 0.1074 | 7258.5 | 0.1074 | 7258.5 | 0.1074 | 7258.5 | 0.1074 | 7258.5 | 0.1074 | 7258.5 | 0.1074 | 7258.5 | 0.1074 | 7258.5 | 0.1074 | 7258.5 | 0.1074 | 7258.5 | 0.1074 | 7258.5 | 0.1074 | 7258.5 | 0.1074
5686.94 | 0.10371 | 5686.94 | 0.10371 | 5686.94 | 0.10371 | 5686.94 | 0.10371 | 7258.5 | 0.13586 | 7258.5 | 0.13586 | 7258.5 | 0.13586 | 7258.5 | 0.13586 | 7258.5 | 0.13586 | 7258.5 | 0.13586 | 7258.5 | 0.13586 | 7258.5 | 0.13586 | 7258.5 | 0.13586 | 7258.5 | 0.13586 | 7258.5 | 0.13586 | 7258.5 | 0.13586
4651.42 | 0.11941 | 4651.42 | 0.11941 | 4651.42 | 0.11941 | 4651.42 | 0.11941 | 7258.5 | 0.15394 | 7258.5 | 0.15394 | 7258.5 | 0.15394 | 7258.5 | 0.15394 | 7258.5 | 0.15394 | 7258.5 | 0.15394 | 7258.5 | 0.15394 | 7258.5 | 0.15394 | 7258.5 | 0.15394 | 7258.5 | 0.15394 | 7258.5 | 0.15394 | 7258.5 | 0.15394
3714.24 | 0.14239 | 3714.24 | 0.14239 | 3714.24 | 0.14239 | 3714.24 | 0.14239 | 6740.76 | 0.16135 | 6740.76 | 0.16135 | 6740.76 | 0.16135 | 6740.76 | 0.16135 | 7258.5 | 0.17253 | 7258.5 | 0.17253 | 7258.5 | 0.17253 | 7258.5 | 0.17253 | 7258.5 | 0.17253 | 7258.5 | 0.17253 | 7258.5 | 0.17253 | 7258.5 | 0.17253
2945.19 | 0.17549 | 2945.19 | 0.17549 | 2945.19 | 0.17549 | 2945.19 | 0.17549 | 5485.85 | 0.18616 | 5485.85 | 0.18616 | 5485.85 | 0.18616 | 5485.85 | 0.18616 | 7258.5 | 0.21585 | 7258.5 | 0.21585 | 7258.5 | 0.21585 | 7258.5 | 0.21585 | 7258.5 | 0.21585 | 7258.5 | 0.21585 | 7258.5 | 0.21585 | 7258.5 | 0.21585
2230.38 | 0.23058 | 2230.38 | 0.23058 | 2230.38 | 0.23058 | 2230.38 | 0.23058 | 4637.49 | 0.21094 | 4637.49 | 0.21094 | 4637.49 | 0.21094 | 4637.49 | 0.21094 | 7258.5 | 0.26364 | 7258.5 | 0.26364 | 7258.5 | 0.26364 | 7258.5 | 0.26364 | 7258.5 | 0.26364 | 7258.5 | 0.26364 | 7258.5 | 0.26364 | 7258.5 | 0.26364
1800.69 | 0.28905 | 1800.69 | 0.28905 | 1800.69 | 0.28905 | 1800.69 | 0.28905 | 3644.33 | 0.25713 | 3644.33 | 0.25713 | 3644.33 | 0.25713 | 3644.33 | 0.25713 | 7258.5 | 0.28219 | 7258.5 | 0.28219 | 7258.5 | 0.28219 | 7258.5 | 0.28219 | 7258.5 | 0.28219 | 7258.5 | 0.28219 | 7258.5 | 0.28219 | 7258.5 | 0.28219
1472.81 | 0.36489 | 1472.81 | 0.36489 | 1472.81 | 0.36489 | 1472.81 | 0.36489 | 2664.92 | 0.34814 | 2664.92 | 0.34814 | 2664.92 | 0.34814 | 2664.92 | 0.34814 | 6720.57 | 0.29254 | 6720.57 | 0.29254 | 6720.57 | 0.29254 | 6720.57 | 0.29254 | 7258.5 | 0.30084 | 7258.5 | 0.30084 | 7258.5 | 0.30084 | 7258.5 | 0.30084
1261.34 | 0.42992 | 1261.34 | 0.42992 | 1261.34 | 0.42992 | 1261.34 | 0.42992 | 1978.17 | 0.47135 | 1978.17 | 0.47135 | 1978.17 | 0.47135 | 1978.17 | 0.47135 | 5393.38 | 0.34571 | 5393.38 | 0.34571 | 5393.38 | 0.34571 | 5393.38 | 0.34571 | 7258.5 | 0.38552 | 7258.5 | 0.38552 | 7258.5 | 0.38552 | 7258.5 | 0.38552
1204.63 | 0.45559 | 1204.63 | 0.45559 | 1204.63 | 0.45559 | 1204.63 | 0.45559 | 1532.92 | 0.62365 | 1532.92 | 0.62365 | 1532.92 | 0.62365 | 1532.92 | 0.62365 | 4196.17 | 0.42777 | 4196.17 | 0.42777 | 4196.17 | 0.42777 | 4196.17 | 0.42777 | 7258.5 | 0.48814 | 7258.5 | 0.48814 | 7258.5 | 0.48814 | 7258.5 | 0.48814
1088.9 | 0.51728 | 1088.9 | 0.51728 | 1088.9 | 0.51728 | 1204.63 | 0.6388 | 1262.6 | 0.77402 | 1262.6 | 0.77402 | 1262.6 | 0.77402 | 1262.6 | 0.77402 | 3251.68 | 0.54599 | 3251.68 | 0.54599 | 3251.68 | 0.54599 | 3251.68 | 0.54599 | 7258.5 | 0.54218 | 7258.5 | 0.54218 | 7258.5 | 0.54218 | 7258.5 | 0.54218
978.412 | 0.58557 | 978.412 | 0.58557 | 978.412 | 0.58557 | 1204.63 | 0.85885 | 1204.63 | 0.82765 | 1204.63 | 0.82765 | 1204.63 | 0.82765 | 1204.63 | 0.82765 | 2512.24 | 0.70387 | 2512.24 | 0.70387 | 2512.24 | 0.70387 | 2512.24 | 0.70387 | 5942.76 | 0.62054 | 5942.76 | 0.62054 | 5942.76 | 0.62054 | 5942.76 | 0.62054
875.619 | 0.66354 | 875.619 | 0.66354 | 875.619 | 0.66354 | 1204.63 | 1.2434 | 1079.15 | 0.93038 | 1079.15 | 0.93038 | 1079.15 | 0.93038 | 1204.63 | 0.85885 | 1866.7 | 0.96835 | 1866.7 | 0.96835 | 1866.7 | 0.96835 | 1866.7 | 0.96835 | 4433.43 | 0.78808 | 4433.43 | 0.78808 | 4433.43 | 0.78808 | 4433.43 | 0.78808
780.497 | 0.77247 | 780.497 | 0.77247 | 875.619 | 0.86922 | 1204.63 | 1.6584 | 1000.17 | 1.015 | 1000.17 | 1.015 | 1000.17 | 1.015 | 1204.63 | 1.2434 | 1456.7 | 1.2877 | 1456.7 | 1.2877 | 1456.7 | 1.2877 | 1456.7 | 1.2877 | 3452.76 | 0.98495 | 3452.76 | 0.98495 | 3452.76 | 0.98495 | 3452.76 | 0.98495
716.18 | 0.86143 | 716.18 | 0.86143 | 875.619 | 1.2273 | 1204.63 | 2.4226 | 911.353 | 1.1398 | 911.353 | 1.1398 | 911.353 | 1.1398 | 1204.63 | 1.6584 | 1267.66 | 1.5126 | 1267.66 | 1.5126 | 1267.66 | 1.5126 | 1267.66 | 1.5126 | 2757.08 | 1.2322 | 2757.08 | 1.2322 | 2757.08 | 1.2322 | 2757.08 | 1.2322
659.137 | 0.97029 | 659.137 | 0.97029 | 875.619 | 1.7038 | 1204.63 | 3.2669 | 875.619 | 1.1994 | 875.619 | 1.1994 | 875.619 | 1.1994 | 1204.63 | 2.4226 | 1204.63 | 1.5949 | 1204.63 | 1.5949 | 1204.63 | 1.5949 | 1204.63 | 1.5949 | 2221.48 | 1.5509 | 2221.48 | 1.5509 | 2221.48 | 1.5509 | 2221.48 | 1.5509
585.772 | 1.1745 | 659.137 | 1.0324 | 875.619 | 2.4617 | 1204.63 | 6.9091 | 780.497 | 1.3797 | 780.497 | 1.3797 | 875.619 | 1.2273 | 1204.63 | 3.2669 | 1071.62 | 1.831 | 1071.62 | 1.831 | 1071.62 | 1.831 | 1204.63 | 1.6584 | 1757.99 | 2.0014 | 1757.99 | 2.0014 | 1757.99 | 2.0014 | 1757.99 | 2.0014
536.427 | 1.3296 | 659.137 | 1.3163 | 875.619 | 3.4689 | 1204.63 | 17.599 | 716.18 | 1.5401 | 716.18 | 1.5401 | 875.619 | 1.7038 | 1204.63 | 6.9091 | 985.285 | 2.0134 | 985.285 | 2.0134 | 985.285 | 2.0134 | 1204.63 | 2.4226 | 1352.79 | 2.6989 | 1352.79 | 2.6989 | 1352.79 | 2.6989 | 1352.79 | 2.6989
488.789 | 1.5997 | 659.137 | 1.8091 | 875.619 | 4.859 | 1204.63 | 60.9984 | 665.761 | 1.7038 | 665.761 | 1.7038 | 875.619 | 2.4617 | 1204.63 | 17.599 | 916.838 | 2.2296 | 916.838 | 2.2296 | 916.838 | 2.2296 | 1204.63 | 3.2669 | 1204.63 | 3.1014 | 1204.63 | 3.1014 | 1204.63 | 3.1014 | 1204.63 | 3.1014
451.209 | 1.8717 | 659.137 | 2.5827 | 875.619 | 10.7708 | 1204.63 | 240.291 | 659.137 | 1.7469 | 659.137 | 1.7469 | 875.619 | 3.4689 | 1204.63 | 60.9984 | 875.619 | 2.3604 | 875.619 | 2.3604 | 875.619 | 2.3604 | 1204.63 | 6.9091 | 1074.84 | 3.5889 | 1074.84 | 3.5889 | 1074.84 | 3.5889 | 1204.63 | 3.2669
443.604 | 2.0014 | 659.137 | 3.6577 | 875.619 | 24.1394 | 1204.63 | 1000.1 | 586.945 | 2.0685 | 659.137 | 1.8091 | 875.619 | 4.859 | 1204.63 | 240.291 | 786.766 | 2.6881 | 786.766 | 2.6881 | 875.619 | 2.4617 | 1204.63 | 17.599 | 1004.18 | 3.9034 | 1004.18 | 3.9034 | 1004.18 | 3.9034 | 1204.63 | 6.9091
443.604 | 2.2838 | 659.137 | 5.338 | 875.619 | 81.0324 |  |  | 530.029 | 2.4178 | 659.137 | 2.5827 | 875.619 | 10.7708 | 1204.63 | 1000.1 | 735.78 | 2.9149 | 735.78 | 2.9149 | 875.619 | 3.4689 | 1204.63 | 60.9984 | 944.76 | 4.2412 | 944.76 | 4.2412 | 944.76 | 4.2412 | 1204.63 | 17.599
443.604 | 3.571 | 659.137 | 7.3437 | 875.619 | 249.099 |  |  | 477.675 | 2.9266 | 659.137 | 3.6577 | 875.619 | 24.1394 |  |  | 688.098 | 3.2086 | 688.098 | 3.2086 | 875.619 | 4.859 | 1204.63 | 240.291 | 898.683 | 4.5034 | 898.683 | 4.5034 | 898.683 | 4.5034 | 1204.63 | 60.9984
443.604 | 4.6452 | 659.137 | 18.2077 | 876.495 | 1000.1 |  |  | 449.408 | 3.3429 | 659.137 | 5.338 | 875.619 | 81.0324 |  |  | 659.137 | 3.4207 | 659.137 | 3.4207 | 875.619 | 10.7708 | 1204.63 | 1000.1 | 875.619 | 4.6779 | 875.619 | 4.6779 | 875.619 | 4.6779 | 1204.63 | 240.291
443.604 | 6.4938 | 659.137 | 55.3042 |  |  |  |  | 443.604 | 3.4551 | 659.137 | 7.3437 | 875.619 | 249.099 |  |  | 585.772 | 3.9942 | 659.137 | 3.6577 | 875.619 | 24.1394 |  |  | 789.13 | 5.3916 | 789.13 | 5.3916 | 875.619 | 4.859 | 1204.63 | 1000.1
443.604 | 9.5434 | 659.137 | 227.659 |  |  |  |  | 443.604 | 3.571 | 659.137 | 18.2077 | 876.495 | 1000.1 |  |  | 538.577 | 4.5305 | 659.137 | 5.338 | 875.619 | 81.0324 |  |  | 745.407 | 5.7537 | 745.407 | 5.7537 | 875.619 | 10.7708
443.604 | 14.4377 | 659.137 | 1000.1 |  |  |  |  | 443.604 | 4.6452 | 659.137 | 55.3042 |  |  |  |  | 477.198 | 5.4132 | 659.137 | 7.3437 | 875.619 | 249.099 |  |  | 709.053 | 6.2142 | 709.053 | 6.2142 | 875.619 | 24.1394
443.604 | 36.3374 | [6 empty] | 443.604 | 6.4938 | 659.137 | 227.659 |  |  |  |  | 450.758 | 5.9408 | 659.137 | 18.2077 | 876.495 | 1000.1 |  |  | 678.532 | 6.6648 | 678.532 | 6.6648 | 875.619 | 81.0324
443.604 | 132.138 | [6 empty] | 443.604 | 9.5434 | 659.137 | 1000.1 |  |  |  |  | 443.604 | 6.1095 | 659.137 | 55.3042 |  |  |  |  | 659.137 | 6.9368 | 659.137 | 6.9368 | 875.619 | 249.099
443.604 | 424.05 | [6 empty] | 443.604 | 14.4377 | [6 empty] | 443.604 | 6.4938 | 659.137 | 227.659 |  |  |  |  | 586.945 | 8.2223 | 659.137 | 7.3437 | 876.495 | 1000.1
443.604 | 1000.1 | [6 empty] | 443.604 | 36.3374 | [6 empty] | 443.604 | 9.5434 | 659.137 | 1000.1 |  |  |  |  | 533.218 | 9.572 | 659.137 | 18.2077
[8 empty] | 443.604 | 132.138 | [6 empty] | 443.604 | 14.4377 | [6 empty] | 481.994 | 11.3912 | 659.137 | 55.3042
[8 empty] | 443.604 | 424.05 | [6 empty] | 443.604 | 36.3374 | [6 empty] | 458.028 | 12.6777 | 659.137 | 227.659
[8 empty] | 443.604 | 1000.1 | [6 empty] | 443.604 | 132.138 | [6 empty] | 443.604 | 13.4213 | 659.137 | 1000.1
[16 empty] | 443.604 | 424.05 | [6 empty] | 443.604 | 14.4377
[16 empty] | 443.604 | 1000.1 | [6 empty] | 443.604 | 36.3374
[24 empty] | 443.604 | 132.138
[24 empty] | 443.604 | 424.05
[24 empty] | 443.604 | 1000.1