## 685-9-2
S&C Vista Underground Distribution Switchgear Overcurrent Control | [9 empty] | S&C Vista Underground Distribution Switchgear Overcurrent Control
Tap Interrupter Speed (TCC 685-9-2) | [9 empty] | Tap Interrupter Speed (TCC 685-9-2)
Total Clearing Time-Current Characteristic Curves Dated February 16, 2009 | [9 empty] | Total Clearing Time-Current Characteristic Curves Dated February 16, 2009
Tolerance in Terms of Current: Curves are plotted to maximum test points. All variations are minus. | [9 empty] | Tolerance in Terms of Current: Curves are plotted to maximum test points. All variations are minus.
50A |  | 65A |  | 80A |  | 100A |  | 150A |  | 200A |  | 250A |  | 300A |  | 350A |  | 400A
Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time
25000 | 0.04 | 25000 | 0.04 | 25000 | 0.04 | 25000 | 0.04 | 25000 | 0.04 | 25000 | 0.04 | 25000 | 0.04 | 25000 | 0.04 | 25000 | 0.04 | 25000 | 0.04
16000 | 0.04 | 16000 | 0.04 | 16000 | 0.04 | 16000 | 0.04 | 16000 | 0.04 | 16000 | 0.04 | 16000 | 0.04 | 16000 | 0.04098 | 16000 | 0.0419 | 16000 | 0.0431
3122.1446 | 0.04 | 3932.0541 | 0.04 | 4947.1446 | 0.04 | 6145.5256 | 0.04 | 8951.9495 | 0.04 | 12196.3857 | 0.04 | 15072.9527 | 0.04 | 13125.2912 | 0.042 | 15554.7224 | 0.042 | 14000 | 0.044
2161.4847 | 0.042 | 2722.1913 | 0.042 | 3424.9463 | 0.042 | 4254.5947 | 0.042 | 6197.5035 | 0.042 | 8443.6517 | 0.042 | 10435.1211 | 0.042 | 10208.5598 | 0.044 | 12098.1174 | 0.044 | 11845.158 | 0.046
1681.1548 | 0.044 | 2117.2599 | 0.044 | 2663.8471 | 0.044 | 3309.1292 | 0.044 | 4820.2805 | 0.044 | 6567.2846 | 0.044 | 8116.2053 | 0.044 | 8637.286 | 0.0461 | 10236.008 | 0.046 | 10707.881 | 0.0473
1422.396 | 0.046 | 1791.377 | 0.0462 | 2253.835 | 0.0461 | 2799.797 | 0.0461 | 4078.356 | 0.046 | 5556.466 | 0.0461 | 6866.981 | 0.0462 | 7922.73 | 0.0471 | 9275 | 0.0472 | 9649.624 | 0.0487
1340 | 0.0466 | 1421.761 | 0.0493 | 1974.707 | 0.0479 | 2515.145 | 0.0474 | 3584.398 | 0.0477 | 4945.927 | 0.0475 | 6143.693 | 0.0476 | 7274.854 | 0.0484 | 8590 | 0.0484 | 8614.893 | 0.0506
1260 | 0.0473 | 1215.634 | 0.0521 | 1715.799 | 0.0501 | 2212.88 | 0.0491 | 3170.008 | 0.0494 | 4388.925 | 0.0492 | 5311.115 | 0.0497 | 6522.01 | 0.05 | 7818.389 | 0.0498 | 7731.238 | 0.0527
1260 | 0.0473 | 1125.886 | 0.0537 | 1492.389 | 0.0525 | 1940.871 | 0.0512 | 2762.956 | 0.0519 | 3915.413 | 0.0512 | 4615.307 | 0.0522 | 5914.375 | 0.0517 | 7112.209 | 0.0515 | 7010.799 | 0.0549
1175 | 0.0481 | 1007.372 | 0.0562 | 1364.582 | 0.0544 | 1712.962 | 0.0537 | 2515.816 | 0.0538 | 3580 | 0.053 | 4142.09 | 0.0545 | 5363.351 | 0.0536 | 6564.728 | 0.0531 | 6066.652 | 0.0587
1100 | 0.0491 | 899.32 | 0.0594 | 1249.02 | 0.0564 | 1519.705 | 0.0564 | 2170.056 | 0.0575 | 3180 | 0.0557 | 3690.424 | 0.0574 | 4894.12 | 0.0557 | 5950 | 0.0551 | 5348.911 | 0.0628
1030 | 0.05 | 788.774 | 0.0638 | 1123.189 | 0.0594 | 1402.651 | 0.0586 | 1945.18 | 0.061 | 2784.706 | 0.0592 | 3257.371 | 0.0609 | 4419.719 | 0.0584 | 5494.913 | 0.0573 | 4730.832 | 0.06768
980 | 0.0509 | 715.25 | 0.06804 | 1037.748 | 0.0619 | 1290.576 | 0.0611 | 1706.16 | 0.0658 | 2387.303 | 0.0645 | 2957.027 | 0.0645 | 4020.477 | 0.0612 | 4967.494 | 0.06 | 4227.941 | 0.07404
932 | 0.0518 | 626.026 | 0.07548 | 941.006 | 0.0654 | 1150 | 0.0655 | 1534.259 | 0.07188 | 2200 | 0.06828 | 2725 | 0.06828 | 3645.902 | 0.0647 | 4618.619 | 0.0625 | 3790.322 | 0.08172
882 | 0.0528 | 557.135 | 0.08388 | 849.737 | 0.07056 | 1032.327 | 0.0708 | 1379.769 | 0.07884 | 2037.539 | 0.07224 | 2477.76 | 0.07368 | 3295.921 | 0.06948 | 4240.972 | 0.0658 | 3447.866 | 0.08952
833.065 | 0.054 | 497.375 | 0.09372 | 771.325 | 0.07668 | 920.152 | 0.07776 | 1254.511 | 0.08652 | 1854.007 | 0.078 | 2232.982 | 0.08052 | 3007.567 | 0.07464 | 3947.226 | 0.06948 | 3090.99 | 0.0996
767.307 | 0.0557 | 446.343 | 0.1056 | 681.451 | 0.0864 | 829.187 | 0.08652 | 1137.868 | 0.0948 | 1672.552 | 0.08568 | 2018.674 | 0.08832 | 2767.377 | 0.08064 | 3628.249 | 0.07452 | 2800.039 | 0.10992
714.877 | 0.0576 | 400.963 | 0.11976 | 610.253 | 0.0972 | 747.214 | 0.09684 | 1030.33 | 0.10584 | 1519.885 | 0.09444 | 1789.222 | 0.09924 | 2475.836 | 0.08952 | 3391.024 | 0.07884 | 2520.837 | 0.12492
648.923 | 0.0602 | 351.311 | 0.14148 | 552.788 | 0.10884 | 672.644 | 0.10848 | 933.566 | 0.11928 | 1354.119 | 0.10668 | 1610.788 | 0.11196 | 2226.561 | 0.09888 | 3123.486 | 0.0852 | 2275.558 | 0.14088
609.637 | 0.0623 | 318.896 | 0.16056 | 493.489 | 0.12468 | 599.87 | 0.12348 | 850.081 | 0.13452 | 1226.683 | 0.11892 | 1427.698 | 0.12828 | 1996.143 | 0.11196 | 2874.064 | 0.09288 | 2077.112 | 0.15708
566 | 0.0657 | 287.474 | 0.18552 | 449.82 | 0.14052 | 538.882 | 0.14136 | 767.726 | 0.15288 | 1120.528 | 0.1326 | 1281.313 | 0.14748 | 1831.004 | 0.12336 | 2639.063 | 0.10104 | 1917.172 | 0.17664
504.432 | 0.07104 | 263.036 | 0.21396 | 405.768 | 0.16056 | 485.103 | 0.16272 | 686.076 | 0.17868 | 1021.559 | 0.14964 | 1177.78 | 0.1644 | 1679.527 | 0.13692 | 2395.705 | 0.11184 | 1742.142 | 0.20124
468.499 | 0.0756 | 238.021 | 0.25596 | 368.27 | 0.1842 | 440.802 | 0.18564 | 610.561 | 0.21132 | 909.083 | 0.1752 | 1090.524 | 0.18444 | 1535.78 | 0.15324 | 2177.052 | 0.12444 | 1583.091 | 0.23424
440.136 | 0.08028 | 218.4479 | 0.3015 | 333.947 | 0.21168 | 401.381 | 0.21588 | 554.214 | 0.24612 | 846.11 | 0.19524 | 987.863 | 0.2136 | 1386.912 | 0.17556 | 1993 | 0.13728 | 1446.9543 | 0.2709
400.362 | 0.08784 | 203.3086 | 0.3482 | 304.751 | 0.24468 | 365.6994 | 0.2511 | 505.4522 | 0.2894 | 765.686 | 0.22584 | 913.775 | 0.2454 | 1270.851 | 0.19824 | 1839.412 | 0.15252 | 1320.3366 | 0.3198
380.059 | 0.09372 | 191.5958 | 0.3917 | 279.103 | 0.2851 | 339.2928 | 0.2888 | 464.9799 | 0.3424 | 703.804 | 0.26124 | 837.8711 | 0.2832 | 1185.359 | 0.22368 | 1681.997 | 0.17328 | 1228.8573 | 0.3688
356.679 | 0.10044 | 176.6545 | 0.472 | 256.2659 | 0.332 | 316.4359 | 0.3301 | 424.3415 | 0.4061 | 652.0657 | 0.3033 | 771.7732 | 0.3335 | 1084.965 | 0.25416 | 1525.306 | 0.19896 | 1142.526 | 0.4321
325.14 | 0.11148 | 164.582 | 0.555 | 237.7595 | 0.3839 | 290.2449 | 0.3967 | 394.515 | 0.4767 | 587.0238 | 0.3756 | 709.4021 | 0.3973 | 1033.8438 | 0.2786 | 1404.965 | 0.22428 | 1057.848 | 0.5121
297.285 | 0.12384 | 152.5392 | 0.67 | 215.3701 | 0.4771 | 268.1679 | 0.4733 | 365.6411 | 0.5634 | 548.0684 | 0.438 | 669.2697 | 0.4533 | 959.2297 | 0.3222 | 1298.164 | 0.25788 | 984.555 | 0.6038
275.675 | 0.13596 | 141.0838 | 0.8095 | 195.0894 | 0.579 | 243.6775 | 0.5739 | 336.7705 | 0.679 | 512.1666 | 0.5146 | 624.8649 | 0.5359 | 877.1312 | 0.3826 | 1205 | 0.2929 | 907.7981 | 0.7209
256.173 | 0.15 | 130.1003 | 0.9685 | 178.9403 | 0.6994 | 224.4407 | 0.6931 | 315.3898 | 0.8001 | 482.7372 | 0.592 | 573.7776 | 0.6507 | 812.9814 | 0.4505 | 1133 | 0.3317 | 844.0234 | 0.8576
239.415 | 0.16524 | 120.5556 | 1.1695 | 165.3278 | 0.8385 | 208.8856 | 0.821 | 292.611 | 0.9524 | 448.8308 | 0.6913 | 524.6791 | 0.7978 | 752.7399 | 0.5384 | 1051.7111 | 0.3888 | 796.2438 | 1.0059
222.437 | 0.183 | 113.4991 | 1.392 | 155.1902 | 0.9954 | 193.6011 | 0.9893 | 274.3642 | 1.1234 | 419.4817 | 0.818 | 483.2883 | 0.9758 | 704.2508 | 0.622 | 997.3678 | 0.4396 | 750.6477 | 1.1965
209.116 | 0.20124 | 106.9607 | 1.6411 | 144.5092 | 1.2106 | 183.0191 | 1.1333 | 257.7069 | 1.3369 | 392.0521 | 0.965 | 449.3489 | 1.1771 | 664.3923 | 0.7101 | 934.098 | 0.5134 | 704.9735 | 1.3969
192.81 | 0.22716 | 100.1715 | 1.9678 | 133.4575 | 1.5152 | 170.1568 | 1.3639 | 243.6181 | 1.6086 | 362.2465 | 1.1736 | 424.3635 | 1.3783 | 610.0622 | 0.8644 | 866.69 | 0.6012 | 666.0412 | 1.6707
182.8057 | 0.2482 | 93.3262 | 2.4223 | 124.7136 | 1.8276 | 160.1875 | 1.6428 | 230.7789 | 1.907 | 337.5042 | 1.4374 | 395.3851 | 1.7101 | 571.3576 | 1.0399 | 818.4935 | 0.6896 | 629.1428 | 1.9789
171.3393 | 0.2804 | 88.6853 | 2.8746 | 117.5262 | 2.2125 | 149.864 | 2.0273 | 218.845 | 2.2411 | 319.3971 | 1.7018 | 373.0111 | 2.0152 | 532.8873 | 1.2522 | 759.4279 | 0.8217 | 598.0601 | 2.3281
158.1437 | 0.3252 | 84.7154 | 3.4159 | 113.5354 | 2.5113 | 141.6723 | 2.4881 | 209.6996 | 2.6345 | 299.2627 | 2.0598 | 355.2142 | 2.3977 | 502.2039 | 1.5108 | 719.4385 | 0.9282 | 564.6333 | 2.8318
148.7244 | 0.3727 | 81.2603 | 4.0267 | 109.3587 | 2.8716 | 133.7897 | 2.9989 | 199.8931 | 3.1205 | 282.7616 | 2.4816 | 337.2127 | 2.9529 | 473.2882 | 1.8054 | 682.264 | 1.0575 | 539.7579 | 3.3374
137.4131 | 0.4418 | 79.255 | 4.522 | 104.7893 | 3.3494 | 128.1995 | 3.6009 | 193.9476 | 3.5327 | 269.8696 | 2.9512 | 322.4617 | 3.5748 | 449.911 | 2.1256 | 642.9841 | 1.253 | 526.2675 | 3.798
129.074 | 0.5026 | 77.6226 | 5.169 | 99.9933 | 4.0855 | 123.4167 | 4.334 | 188.1946 | 4.0877 | 260.4789 | 3.4855 | 311.2571 | 4.2933 | 425.8672 | 2.5558 | 601.8782 | 1.5086 | 506.5434 | 4.6674
123.8303 | 0.5584 | 76.1816 | 6.1088 | 96.4161 | 5.042 | 121.2739 | 5.0107 | 182.6847 | 4.8751 | 251.1641 | 4.1906 | 302.0083 | 5.0307 | 409.563 | 3.0363 | 562.2375 | 1.8363 | 489.4285 | 5.7076
115.3691 | 0.6538 | 74.5338 | 7.48 | 93.6463 | 6.0646 | 117.1555 | 6.052 | 177.5334 | 5.7195 | 240.658 | 5.2422 | 294.5624 | 5.8896 | 392.4404 | 3.6383 | 537.0827 | 2.1488 | 469.0378 | 7.1948
107.822 | 0.7519 | 73.7627 | 8.9162 | 91.8115 | 7.1384 | 114.6354 | 7.2279 | 173.8528 | 6.8164 | 234.6795 | 6.2147 | 287.3002 | 7.1884 | 381.986 | 4.2891 | 510.9225 | 2.5677 | 459.4898 | 8.5405
101.5047 | 0.8733 | 72.6011 | 10.4757 | 90.6719 | 8.4823 | 112.8314 | 8.7146 | 169.73 | 8.4171 | 227.8518 | 7.9577 | 281.3844 | 8.7024 | 369.5329 | 5.1312 | 488.0634 | 3.0662 | 448.7835 | 10.097
95.7583 | 1.0141 | 72.0423 | 12.2832 | 89.4531 | 10.228 | 110.8371 | 10.3997 | 166.9448 | 10.1075 | 223.6872 | 9.8994 | 276.7402 | 10.3198 | 357.9917 | 6.3604 | 466.2273 | 3.7162 | 443.9094 | 12.0129
90.8072 | 1.1546 | 71.5 | 15.6056 | 88.7117 | 12.2832 | 110.2299 | 12.0177 | 165.3872 | 12.1512 | 220.7645 | 12.0254 | 275.55 | 12.6532 | 345.972 | 7.8286 | 450.4863 | 4.247 | 440 | 14.5183
85.844 | 1.3438 | 71.5 | 20.6079 | 88 | 14.4034 | 110 | 14.2099 | 165 | 14.5183 | 220 | 13.6535 | 275 | 15.6291 | 338.3842 | 9.4293 | 436.1764 | 5.0702 | 440 | 17.8425
81.1525 | 1.5922 | 71.5 | 26.1874 | 88 | 16.9435 | 110 | 18.1111 | 165 | 17.5111 | 220 | 16.6227 | 275 | 18.9876 | 332.3551 | 11.4415 | 426.591 | 5.7899 | 440 | 22.602
76.7173 | 1.9031 | 71.5 | 30.7778 | 88 | 20.0155 | 110 | 22.9658 | 165 | 20.9251 | 220 | 20.8163 | 275 | 21.3583 | 330 | 13.9714 | 410.927 | 6.972 | 440 | 30.2908
72.9025 | 2.2573 | 71.5 | 40.3573 | 88 | 25.1971 | 110 | 29.0634 | 165 | 24.9276 | 220 | 27.6653 | 275 | 28.0588 | 330 | 17.5669 | 401.6122 | 8.2583 | 440 | 40.7259
72.6 | 2.2619 | 71.5 | 50.6014 | 88 | 31.0031 | 110 | 37.4005 | 165 | 31.7122 | 220 | 35.086 | 275 | 37.7978 | 330 | 22.9098 | 393.2984 | 9.8851 | 440 | 53.4061
69.7114 | 2.6564 | 71.5 | 63.1837 | 88 | 41.036 | 110 | 47.7817 | 165 | 39.472 | 220 | 45.4843 | 275 | 50.9208 | 330 | 28.631 | 388.52 | 12.0071 | 440 | 66.618
67.3585 | 3.0316 | 71.5 | 78.1595 | 88 | 53.6995 | 110 | 61.9443 | 165 | 47.3718 | 220 | 60.8407 | 275 | 65.8021 | 330 | 36.7656 | 385 | 14.405 | 440 | 87.5482
65.3466 | 3.4711 | 71.5 | 97.2934 | 88 | 69.1831 | 110 | 79.4744 | 165 | 58.1125 | 220 | 80.5407 | 275 | 84.1533 | 330 | 47.6588 | 385 | 17.5368 | 440 | 109.6678
63.3468 | 3.9833 | 71.5 | 124.3124 | 88 | 85.7602 | 110 | 100.1761 | 165 | 69.9643 | 220 | 103.8787 | 275 | 103.2292 | 330 | 62.5597 | 385 | 21.8912 | 440 | 137.3778
62.0411 | 4.5669 | 71.5 | 156.3716 | 88 | 110.4934 | 110 | 125.7467 | 165 | 86.5497 | 220 | 138.2402 | 275 | 130.9264 | 330 | 79.428 | 385 | 29.152 | 440 | 169.0668
60.511 | 5.3133 | 71.5 | 200.8466 | 88 | 140.5915 | 110 | 157.0253 | 165 | 108.0781 | 220 | 180.9265 | 275 | 165.8842 | 330 | 99.1784 | 385 | 40.5612 | 440 | 212.4532
59.4495 | 5.9681 | 71.5 | 247.1745 | 88 | 179.451 | 110 | 194.254 | 165 | 136.5208 | 220 | 233.8511 | 275 | 203.7058 | 330 | 130.7418 | 385 | 51.9252 | 440 | 274.0291
58.2714 | 6.7952 | 71.5 | 301.348 | 88 | 227.8623 | 110 | 237.0746 | 165 | 171.7327 | 220 | 300.0607 | 275 | 258.6391 | 330 | 165.4847 | 385 | 64.0937 | 440 | 346.8797
57.1021 | 8.3128 | 71.5 | 381.0563 | 88 | 289.0343 | 110 | 304.1901 | 165 | 219.6642 | 220 | 381.4207 | 275 | 336.3587 | 330 | 205.5673 | 385 | 80.0281 | 440 | 419.8391
56.2815 | 9.8686 | 71.5 | 464.5764 | 88 | 371.2483 | 110 | 375.1409 | 165 | 277.4808 | 220 | 469.4154 | 275 | 406.6455 | 330 | 261.5589 | 385 | 98.9926 | 440 | 507.0863
55.6303 | 11.9009 | 71.5 | 538.1822 | 88 | 456.8875 | 110 | 454.0371 | 165 | 356.4163 | 220 | 544.3627 | 275 | 503.5535 | 330 | 330.3829 | 385 | 122.4528 | 440 | 600
55 | 14.1454 | 71.5 | 600 | 88 | 527.0714 | 110 | 529.275 | 165 | 454.0046 | 220 | 600 | 275 | 600 | 330 | 412.9893 | 385 | 154.0227
55 | 16.9372 |  |  | 88 | 600 | 110 | 600 | 165 | 530.3498 |  |  |  |  | 330 | 502.9661 | 385 | 195.3564
55 | 19.9253 | [6 empty] | 165 | 600 |  |  |  |  | 330 | 600 | 385 | 255.9249
55 | 24.8498 | [14 empty] | 385 | 324.6105
55 | 29.7899 | [14 empty] | 385 | 397.8052
55 | 34.7584 | [14 empty] | 385 | 502.9974
55 | 39.7611 | [14 empty] | 385 | 600
55 | 49.9588
55 | 59.8341
55 | 69.9643
55 | 79.9549
55 | 99.3231
55 | 120.4603
55 | 149.0212
55 | 188.8317
55 | 188.6348
55 | 296.947
55 | 394.3675
55 | 497.6537
55 | 592.9766
55 | 600